## Slide 1
Corrosion Management of Preaction Fire Sprinkler Systems - Mission Critical Environments
Presented By:

## Slide 2
No. 1 reason automatic sprinklers activate and DO NOT control the fire is not enough water at the sprinkler
Oxygen in the air is the primary cause of corrosion in all water-based fire sprinkler systems
Understanding the chemistry and physics of the oxygen corrosion reaction is key to solving the corrosion problem
Removing oxygen from water-based fire sprinkler systems is the key to corrosion control
Galvanized piping is vulnerable to extreme corrosion
Nitrogen inerting to completely remove oxygen stops corrosion in fire sprinkler systems
Governing bodies are adopting nitrogen inerting technologies including NFPA, FM Global, US DoD, US GSA
Learning Objectives

## Slide 3
Fire Sprinkler Corrosion does not just cause leaks. Corrosion impedes water delivery to the fire!

## Slide 4
NFPA July 2017 Research Report
“U.S. Experience With Sprinklers”
https://www.nfpa.org/-/media/Files/News-and-Research/Fire-statistics/Fire-Protection-Systems/ossprinklers.pdf
Sprinklers 96% effective when they operate
No. 1 cause for failure to control - System Shut Off
When Sprinklers Operate But Are Ineffective at Control
No. 1 cause (51%) - Water did not reach fire
No. 2 cause (30%) - Not enough water discharged

## Slide 5
Debris from Dry Pipe Flushing!

## Slide 6
Question: How common is corrosion?
Answer: Virtually all water based fire sprinkler systems are subject to attack by oxygen corrosion.
It is everywhere!
Corrosion in Fire Sprinkler Systems

## Slide 7
The Science of Corrosion
Oxygen is the Primary Cause of Corrosion in Sprinkler Systems Atmospheric Air: ~21% O2
Steel Piping
Liquid Water
Oxygen
Rust (Iron Oxide Fe2O3)

## Slide 8
Preaction System: Sprinkler system employing closed automatic sprinklers connected to a piping system containing pressurized supervisory gas used in conjunction with a supplemental detection system
Supervisory gas typically compressed air
Two (2) discreet events must occur to release water into system piping (i.e. smoke + heat detection)
Preaction Systems – An Overview

## Slide 9
Water Sources:
Condensate from compressed air source
  Warm, saturated air input to preaction system by air compressor
Hydro-testing of system
  Preaction system integrity is hydrostatically tested immediately after install
  Water never completely removed post-testing
Trip-testing of system
  Preaction system is intentionally activated for verification that water will reach most remote point of system in required amount of time
  Water never completely removed post-testing
Presence of Water in Preaction Systems
ALL PREACTION SYSTEMS TRAP WATER!

## Slide 10
PREACTION SYSTEMS: THE PERFECT ENVIRONMENT FOR OXYGEN CORROSION!
Metallurgy of piping completely susceptible to corrosion
  Black steel or galvanized most typically used
Unlimited source of corrosive oxygen gas
  Air compressor provides constant stream of 20.9% oxygen
Trace amounts of water in piping
  Corrosive activity will only occur where liquid water is present
Piping + unlimited supply O2 + small pools of water = highly localized aggressive pitting of sprinkler piping!
Corrosion of Preaction Systems

## Slide 11
Corrosion-Related Risks
Evaluation of Risk Associated with Corrosion in Fire Sprinkler Systems
Business loss due to fire and/or water damage from leak
  Mission critical facility downtime via equipment damage ($$$)
Life safety injury or loss of life
  Insufficient/no flow to sprinkler heads in fire situation
Property damage or property loss
Business disruption due to cleanup
4” Preaction Main – Half Full of Deposits

## Slide 12: The Most Common Myths Regarding Corrosion
MIC (Microbiologically Influenced Corrosion) is the primary cause of leaks in fire sprinkler systems.
  Bacteria are always present, but oxygen is the primary cause of corrosion in fire sprinkler systems1.
Bad Water causes fire sprinkler system leaks.
  Almost all fire supply water comes from fresh, clean municipal water supplies that are not chemically corrosive.
Materially Defective Sprinkler Pipe causes leaks, particularly at the weld seam.
  Pipe materials used today meet or exceed ASTM requirements incorporated in NFPA 13. Root cause analysis very rarely identifies material defect as the cause of failure.
Pervasive myths regarding corrosion have hindered the implementation of effective corrosion control strategies in fire sprinkler systems.
1 “Corrosion and Corrosion Mitigation in Fire Protection Systems” by Paul Su and David Fuller., FM Global Technical Report- July 2014

## Slide 13: Myth - The Case of Galvanized Steel Sprinkler Pipe
Galvanized Pipe Leak
The use of black steel pipe with a nitrogen generator as the source of supervisory gas is the most effective method of corrosion control in dry pipe and pre-action fire sprinkler systems and is supported by FM Global.1
1 FM Global Property Loss Prevention Data Sheet 2-1 - Corrosion in Automatic Sprinkler Systems (October 2016).
Perhaps the most costly myth of all is that galvanized steel piping performs better than black steel to prevent corrosion in dry pipe and pre-action fire sprinkler systems. All dry pipe systems trap water. In areas with trapped water galvanized pipe will fail 3-4 times faster than black steel due to the highly localized nature of oxygen corrosion on galvanized material. Pinhole leaks will form in as little as two (2) years in areas where trapped water collects.
Zno ZnO Zn(OH)2 ZnCO3

## Slide 14: Galvanized Pipe Concerns
Failures occur much faster; 50% life vs. black steel on average
  Not uncommon for first pinhole failure to occur in <5 years
  Failures reported less than one (1) year in service on multiple occasions
Cost – 40% higher than black steel on average
  Higher cost for less corrosion resistance!
Toxicity of discharged water
  High levels of heavy metal contaminant (zinc) in discharge water; way above allowable discharge limits in many jurisdictions
  High zinc levels are highly toxic and possibly deadly for aquatic life

## Slide 15
Metallurgy – too expensive (copper, stainless)
Plastics – restricted by code (light hazard, residential)
Coatings – delamination complications (sprinkler plugging)
Chemical Inhibitors – ineffective, incompatible (designed for flowing systems, degrades plastics and elastomers)
Remove the Corrosive Gas – purge the oxygen
Options for Controlling Corrosion

## Slide 16
Key Documents Timeline
1998 1999 2001 2013 2014 2016 2017 2018 2019
NFPA 13
1st MIC
Mention
NACE
MIC
Pope
NFPA 13
Biocide
Corrosion
Compatible
UFC Code
No Galv
N2 Generator on Preaction
FM Global
Data Sheet 2-1 MIC & Chemical
Treatment
GSA Code
No Galv
FM Global Corrosion
Report
FM Global
N2 Generator
Standard
NFPA 13
Vent on Wet Pipe
FM Global
Data Sheet 2-1
(Oct. 2016)
N2 Generator
(Dry & Pre-Action)
No Chemical
Dept. of Defense
UFC3-600-01
(Nov. 2016)
N2 Generator
(Pre-Action)
Equipment in Riser Rm
No Continuous Venting
GSA
PBS P-100
(Apr. 2017)
N2 Generator
(Dry & Preaction)
Vent on Riser
In-Line Corr. Mon. Fail Safe Vent
Dept. of Defense
UFC3-600-01
(Mar. 2018)
N2 Generator
(Dry)
NFPA 13
Nitrogen to Mitigate Corrosion
Use Approved Nitrogen Generator

## Slide 17
Key Documents
NFPA 13 – 2019 Edition
  Fill dry-pipe or preaction systems with nitrogen as a supervisory gas to mitigate against corrosion
  When using a generator, use an approved nitrogen generator
  Where listed bacterial inhibitors and/or corrosion inhibitors are used they shall be compatible with system components as well compatible with each other
  A single air vent shall be provided on each wet pipe system utilizing metallic pipe
FM Global 2-1 Data Sheet – April 2018
  Pressurize system using FM Approved nitrogen generator
  Black steel acceptable if nitrogen generator used throughout life of system
  Chemical Cleaners and Corrosion Inhibitors can result in accelerated sprinkler corrosion or restricted orifices

## Slide 18
Key Government Documents
DoD Unified Facilities Criteria UFC 3-600-1 – March 2018
  When nitrogen is used, a C-factor of 120 is permitted
  Black steel must be used for addition, repair or relocation of existing systems
  All nitrogen generation equipment must be installed in riser room
  Process involving continuous venting is not permitted
GSA PBS-100 Facilities Standard – July 2018
  Dry-pipe sprinkler systems must incorporate nitrogen inerting process
  Galvanized sprinkler piping is not permitted

## Slide 19
Nitrogen for Dry Pipe Systems
Essential components for dry pipe systems:
A continuous source of nitrogen gas at 98%+ purity – nitrogen generator
An oxygen removal vent to facilitate removal of oxygen from the dry system piping
A “Fill and Purge” breathing protocol to facilitate removal of oxygen from the dry system piping (ECS Only)
Vent at Riser
Nitrogen Generator

## Slide 20
“Fill and Purge” Breathing Method
ECS Only
Fill Cycle
Purge Cycle
All Equipment Including Vent Installed in Riser Room
Dynamic Mixing of Gas - Homogenization of Atmosphere
Fill - Nitrogen Gas Throughout Piping network, No Matter the Complexity
Purge - All Gas Moves Towards the Vent
Sequential “Fill and Purge” Cycles Removes All Oxygen Gas Resulting in Piping Network Nitrogen Inerted
Compatible with all systems (low pressure and high pressure)

## Slide 21
Dry/Pre-action “Fill and Purge” Breathing with Nitrogen
(U.S. Patent 8,720,591 )
Dry Pipe Nitrogen Inerting (DPNI) Process
3-5 psi pressure range
Above low air alarm/trip pressures
Low Air Alarm
Trip Pressure
Breathing Range
PGEN Cut-In Pressure
System AMD Setting
ECS Fill & Purge Breathing
NO Nitrogen Storage Tank Required
PGEN Cut-Out Pressure
NO Compressed Air Dryer Required
All Equipment Installed in Riser Room

## Slide 22
Fill and Purge Breathing vs. Constant Pressure Venting
 | “Fill and Purge” Venting | Constant Pressure Venting
Supervisory Gas Pressure | Digitally Controlled Fluctuation | Static
Vent Location | Riser Room | Remote (Over Protected Area)
Gas Mixing | Throughout | Poor
Oxygen Removal | Complete | Partial

## Slide 23
Nitrogen generators can serve one or more systems from a single location.
Available in wall-mount, skid-mount, or stand-alone configurations.
Nitrogen Generator Basics
Wall-Mount
Skid-Mount
Stand-Alone

## Slide 24
Nitrogen Generator Features
  Important Nitrogen Generator Features
    FM Approved (Standard 1035)
    UL Listed (UL 508A)
    Vent installed at the riser (ECS “Fill and Purge” Breathing Only)
    No nitrogen storage tanks or refrigerated air dryers (ECS Only)
    Standard alarm signals
      Air bypass mode
      Excessive runtime/leak monitoring
    Standard monitoring points
      Nitrogen generator loss of power
      Air bypass mode
      Nitrogen generation mode
      Nitrogen supply line pressure
      Excessive runtime/leak monitoring

## Slide 25
How Nitrogen Generators Work
A high pressure air compressor (100+ psi) provides feed air to a gas separation membrane. The membrane filters out smaller oxygen molecules as waste gas and delivers larger nitrogen molecules (98+%) as end product gas.
Gas Separation Membrane
Air Compressor
Wall Mount

## Slide 26: Membrane Gas Separation
Functional Characteristics
  “Selective permeation”
    Oxygen = “Fast Gas” (smaller, more soluble molecules)
    Nitrogen = “Slow Gas” (larger, less soluble molecules)
  Efficiency increase with temperature increase
Advantages
  Purity and flow rate easily adjustable
  No storage tank required
  Long service life (15-20 years!)
  No maintenance to membrane required during life
  Compact
  Quiet
  Removes water vapor (no air dryer required)
Disadvantages
  Lower flow rates at higher nitrogen purities
TECHNOLOGY TRUSTED BY THE FAA FOR IN-FLIGHT NITROGEN INERTING OF FUEL TANKS IN COMMERCIAL AIRLINERS!

## Slide 27
Life Expectancy – Compressed Air vs. N2
Sprinkler Life Expectancy - Compressed Air
Average time before first reported failure:
Black Steel Sch. 10: ~10-20 years
Black Steel Sch. 40: ~25-30 years
Galvanized Sch. 10: ~5-10 years
Galvanized Sch. 40: ~15-25 years
~10-30 mils/year corrosion expected under compressed air
Sprinkler Life Expectancy – Nitrogen
Corrosion rate: ~1-5 mils/year under nitrogen inerted atmosphere
Expect 6X-8X multiplier on system service life

## Slide 28
Cost Comparison – Compressed Air vs. N2
Installation Costs
Black Steel: $2.00 - $4.00/sq. ft.
Galvanized: $3.00 - $5.00/sq. ft.
Corrosion control cost add: $.25 - $1.00/sq. ft.
  Costs stay on lower end with larger facilities (100,000 sf+)
Black Steel + Nitrogen = a superior less expensive option to traditional galvanized compressed air preaction systems!!

## Slide 29
Equipment Maintenance/Service Life
Air Compressor
Provides supply air for N2 generation
Filter and oil change annually OR every 500 hours
Service kit cost: $185
Nitrogen Generator
Annual compressed air filter change, between 2-4 filters depending on model
Gas separation membrane used by ECS is rated for 20-year service life
Filter kit cost: $295
Oxygen Removal Vent
Annual inspection of Y-strainer for blockage
Annual inspection of in-line filter for debris
2
1
3
4
2
1

## Slide 30
Corrosion Monitoring
What is Corrosion Monitoring?
Implementation of devices used to give real-time corrosion data within Fire Sprinkler Systems
Why is Corrosion Monitoring necessary?
Early warning to prevent risk
Validates effectiveness of corrosion management system
Old Methods
Coupons
  Riser-mounted - Corrosion simulated; not real-time
  Remotely inserted - Not continuously monitored
Wait for leaks
  Leak occurrences not linear
New Methods
In-Line Corrosion Detectors

## Slide 31
Remote Test Station included
In-Line Corrosion Monitoring Device
Thin walled section creates a pressure chamber
  Important Features
  Only UL Listed (UL 2987) method for monitoring corrosion in fire sprinkler systems
  For Dry Pipe, Pre-action and Wet Pipe Systems
  Complete 360o Coverage of Corrosion Detection
  Continuous monitoring of corrosion activity inside fire sprinkler system
  Installed where corrosion is most likely to occur
    Low point mains in dry systems
    High point branch lines in wet systems
  Local and remote monitoring

## Slide 32
CONTACT US
  Contact ECS for 24/7 engineering and technical support
  Office business hours: Monday thru Friday, 8 AM - 5 PM (central time zone)
  Technical information available online
  CAD files available upon request
(314) 432-1377
info@ecscorrosion.com
www.ecscorrosion.com